## Schedules
file_name | page_index | table_index | schedule_name | MECHANICAL ABBREVIATIONS | COL_2 | MECHANICAL SYMBOLS AND LEGEND - AIR SIDE | COL_3 | MECHANICAL ANNOTATIONS | COL_4 | COL_5 | This document is an instrument of service prepared solely for | STREETS | MECHANICAL SHEET LIST | MARK | UNIT TYPE | LOCATION | SUPPLY FAN | MIN OSA | COOLING COIL | COL_8 | COL_9 | COL_10 | COL_11 | HEATING COIL | COL_13 | COL_14 | ELECTRICAL | COL_16 | COL_17 | COL_18 | ASSOCIATED UNIT | WEIGHT | MANUFACTURER | MODEL | NOTES | COOLING | COL_6 | HEATING | COL_12 | MIN OSA (CFM) | COL_7 | HEATING COIL (HEAT PUMP) | COL_15 | COL_19 | COL_20 | COL_21 | COL_22 | OPERATING WEIGHT (LBS) | SERVICE | SIZE | AIRFLOW (CFM) | MIN. FREE AREA | MAX VELOCITY | MAX APD (IN W.C.) | MATERIAL | FACE TYPE | FACE SIZE | MARGIN | FINISH | MAX AIRFLOW | MAX NC | MOUNTING | ESP (IN W.C.) | TANK SIZE (GAL) | TANK CONFIGURATION | ACFM @ 175 PSIG | RPM | VOLTAGE | PHASE | HZ
tmpldvjvsq2.pdf | 2 | 0 |  | ABBREVIATION | DESCRIPTION
tmpldvjvsq2.pdf | 2 | 0 |  | ADA AFF AFG APD BFF BFG BHP BTU/H CFH CFM COP (D) DB DIA DL DN (E) EAT EFF ESP EWT °F FA FB FLA FPM GA GAL GPH GPM HD HP HSPF IBC IMC IPC IE KW LAT LBS LWT MAX MBH MCA MIN MOCP N/A N/C N/O NEC NFPA NIS NTS OFCI PD PRV PSI RH RPM SEER SP SS TDH TFA TFB TYP UBC UL UMC UPC VFD WB WC WG WPD | AMERICANS WITH DISABILITIES ACT ABOVE FINISHED FLOOR ABOVE FINISHED GRADE AIR PRESSURE DROP BELOW FINISHED FLOOR BELOW FINISHED GRADE BRAKE HORSE POWER BRITISH THERMAL UNIT PER HOUR CUBIC FEET PER HOUR CUBIC FEET PER MINUTE COEFFICIENT OF PERFORMANCE DEMOLISHED DRY BULB TEMPERATURE DIAMETER DOOR LOUVER DOWN EXISTING ENTERING AIR TEMPERATURE EFFICIENCY EXTERNAL STATIC PRESSURE ENTERING WATER TEMPERATURE DEGREES FAHRENHEIT FROM ABOVE FROM BELOW FULL LOAD AMPS FEET PER MINUTE GAGE OR GAUGE GALLONS GALLONS PER HOUR GALLONS PER MINUTE HEAD PRESSURE HORSEPOWER HEATING SEASONAL PERFORMANCE FACTOR INTERNATIONAL BUILDING CODE INTERNATIONAL MECHANICAL CODE INTERNATIONAL PLUMBING CODE INVERT ELEVATION BELOW FINISHED FLOOR KILOWATT LEAVING AIR TEMPERATURE POUNDS LEAVING WATER TEMPERATURE MAXIMUM ONE THOUSAND BTUH MINIMUM CIRCUIT AMPS MINIMUM MAXIMUM OVER CURRENT PROTECTION NOT APPLICABLE NORMALLY CLOSED NORMALLY OPEN NATIONAL ELECTRIC CODE NATIONAL FIRE PROTECTION ASSOCIATION NOT IN SCOPE NOT TO SCALE OWNER FURNISHED, CONTRACTOR INSTALLED PRESSURE DROP PRESSURE REDUCING VALVE POUNDS PER SQUARE INCH RELATIVE HUMIDITY REVOLUTIONS PER MINUTE SEASONAL ENERGY EFFICIENCY RATIO STATIC PRESSURE STAINLESS STEEL TOTAL DYNAMIC HEAD TO FLOOR ABOVE TO FLOOR BELOW TYPICAL UNIFORM BUILDING CODE UNDERWRITERS LABORATORIES, INC. UNIFORM MECHANICAL CODE UNIFORM PLUMBING CODE VARIABLE FREQUENCY DRIVE WET BULB TEMPERATURE WATER COLUMN WATER GAUGE WATER PRESSURE DROP
tmpldvjvsq2.pdf | 2 | 1 |  |  | ABBREVIATION | SYMBOL | DESCRIPTION
tmpldvjvsq2.pdf | 2 | 1 |  |  |  |  | SUPPLY AIR DIFFUSER
tmpldvjvsq2.pdf | 2 | 1 |  |  |  |  | RETURN AIR GRILLE
tmpldvjvsq2.pdf | 2 | 1 |  |  |  |  | EXHAUST AIR GRILLE
tmpldvjvsq2.pdf | 2 | 1 |  |  |  |  | ROUND FLEX DUCT
tmpldvjvsq2.pdf | 2 | 1 |  |  | FD | F | FIRE DAMPER
tmpldvjvsq2.pdf | 2 | 1 |  |  | SD | SD | SMOKE DAMPER
tmpldvjvsq2.pdf | 2 | 1 |  |  | FSD | FSD | COMBINATION FIRE/SMOKE DAMPER
tmpldvjvsq2.pdf | 2 | 1 |  |  |  | 12"x12" OR 12"x12" | RECTANGULAR DUCT SIZE, TOP LENGTH BY SIDE LENGTH
tmpldvjvsq2.pdf | 2 | 1 |  |  | MVD |  | MANUAL VOLUME/BALANCING DAMPER
tmpldvjvsq2.pdf | 2 | 1 |  |  |  |  | DUCT WITH INTERNAL INSULATION
tmpldvjvsq2.pdf | 2 | 1 |  |  |  |  | SQUARE TO ROUND DUCT TRANSITION
tmpldvjvsq2.pdf | 2 | 1 |  |  |  |  | DUCT SIZE TRANSITION
tmpldvjvsq2.pdf | 2 | 1 |  |  |  |  | MITERED ELBOW WITH TURNING VANES
tmpldvjvsq2.pdf | 2 | 1 |  |  | SA |  | SUPPLY AIR DUCT DOWN
tmpldvjvsq2.pdf | 2 | 1 |  |  | SA |  | SUPPLY AIR DUCT UP
tmpldvjvsq2.pdf | 2 | 1 |  |  | RA |  | RETURN AIR DUCT DOWN
tmpldvjvsq2.pdf | 2 | 1 |  |  | RA |  | RETURN AIR DUCT UP
tmpldvjvsq2.pdf | 2 | 1 |  |  | EA |  | EXHAUST AIR DUCT DOWN
tmpldvjvsq2.pdf | 2 | 1 |  |  | EA |  | EXHAUST AIR DUCT UP
tmpldvjvsq2.pdf | 2 | 1 |  |  | MD | M | MOTORIZED DAMPER
tmpldvjvsq2.pdf | 2 | 1 |  |  | OPD |  | OPPOSED BLADE DAMPER
tmpldvjvsq2.pdf | 2 | 1 |  |  | RS/RL | RS/RL | REFRIGERANT SUCTION AND LIQUID LINE SET/PIPING
tmpldvjvsq2.pdf | 2 | 2 | [5 empty] | SYMBOL | ABBREVIATION | DESCRIPTION
tmpldvjvsq2.pdf | 2 | 2 | [5 empty] | RTU # |  | MECHANICAL EQUIPMENT - (SEE MECHANICAL SCHEDULE)
tmpldvjvsq2.pdf | 2 | 2 | [5 empty] | 1 M6.1 |  | DETAIL REFERENCE CALLOUT, DETAIL NUMBER AND SHEET
tmpldvjvsq2.pdf | 2 | 2 | [5 empty] | 1 __________ M3.1 |  | SECTION VIEW CALLOUT, DETAIL NUMBER AND SHEET
tmpldvjvsq2.pdf | 2 | 2 | [6 empty] | POC | POINT OF CONNECTION - NEW ITEMS TO EXISTING ITEMS
tmpldvjvsq2.pdf | 2 | 2 | [5 empty] | L-1 |  | PLUMBING FIXTURE SCHEDULE - (SEE SCHEDULE)
tmpldvjvsq2.pdf | 2 | 2 |  |  |  |  | ? |  |  | SHEET NOTES
tmpldvjvsq2.pdf | 2 | 2 | [6 empty] | AP | ACCESS PANEL
tmpldvjvsq2.pdf | 2 | 2 | [7 empty] | DIFFUSER / GRILLE / REGISTER TAG CD-1 (TYPE) EXAMPLE: DESCRIPTION: 12"Ø / 500 (NECK SIZE) / (CFM)
tmpldvjvsq2.pdf | 2 | 2 | [5 empty] | T | TSTAT | THERMOSTAT
tmpldvjvsq2.pdf | 2 | 2 | [5 empty] | RTS |  | ROOM TEMPERATURE SENSOR
tmpldvjvsq2.pdf | 2 | 2 | [5 empty] | CO |  | CARBON MONOXIDE SENSOR
tmpldvjvsq2.pdf | 2 | 2 | [5 empty] | CO2 |  | CARBON DIOXIDE SENSOR
tmpldvjvsq2.pdf | 2 | 2 | [5 empty] | NO2 |  | NITROGEN DIOXIDE SENSOR
tmpldvjvsq2.pdf | 2 | 2 | [5 empty] | BD |  | BACKDRAFT DAMPER
tmpldvjvsq2.pdf | 2 | 2 | [5 empty] | SD |  | DUCT MOUNTED SMOKE DETECTOR
tmpldvjvsq2.pdf | 2 | 2 | [5 empty] | TCP |  | TEMPERATURE CONTROL PANEL
tmpldvjvsq2.pdf | 2 | 2 | [5 empty] | TS |  | TEMPERATURE SENSOR
tmpldvjvsq2.pdf | 2 | 2 | [5 empty] | DP |  | DIFFERENTIAL PRESSURE SENSOR
tmpldvjvsq2.pdf | 2 | 2 | [5 empty] | ES |  | EMERGENCY SHUTDOWN SWITCH
tmpldvjvsq2.pdf | 2 | 3 | [8 empty] | Kimley-Horn's client and for a particular purpose. Any other
tmpldvjvsq2.pdf | 2 | 3 | [8 empty] | use or reliance is without liability to Kimley-Horn.
tmpldvjvsq2.pdf | 2 | 4 | [9 empty] | DIVISION
tmpldvjvsq2.pdf | 2 | 7 |  |  | SHEET NAME | [7 empty] | SHEET NUMBER
tmpldvjvsq2.pdf | 2 | 7 |  |  | MECHANICAL NOTES, SYMBOLS, AND LEGENDS | [7 empty] | M0.1
tmpldvjvsq2.pdf | 2 | 7 |  |  | MECHANICAL SCHEDULES (1 OF 2) | [7 empty] | M0.2
tmpldvjvsq2.pdf | 2 | 7 |  |  | MECHANICAL SCHEDULES (2 OF 2) | [7 empty] | M0.3
tmpldvjvsq2.pdf | 2 | 7 |  |  | MECHANICAL FLOOR PLAN - GROUND FLOOR | [7 empty] | M2.1
tmpldvjvsq2.pdf | 2 | 7 |  |  | MECHANICAL FLOOR PLAN - MEZZANINE | [7 empty] | M2.2
tmpldvjvsq2.pdf | 2 | 7 |  |  | MECHANICAL PIPING PLAN - GROUND FLOOR | [7 empty] | M2.3
tmpldvjvsq2.pdf | 2 | 7 |  |  | MECHANICAL DETECTION PLAN | [7 empty] | M2.5
tmpldvjvsq2.pdf | 2 | 7 |  |  | MECHANICAL DETAILS | [7 empty] | M6.1
tmpldvjvsq2.pdf | 3 | 0 | NOTES: 1. PROVIDE WITH MANUFACTURER'S STANDARD REMOTE CONTROLLER (PREMTB100). 2. PROVIDE WITH HIGH EFFICIENCY FILTER BOX (ZFBXM101A). 3.UNIT PROVIDED WITH FACTORY INSTALLED CONDENSATE PUMP. 4. PROVIDE WITH AUXILIARY HEATING KIT (PRAH1). | [13 empty] | ESP (IN W.C) |  | TOTAL CAP (MBH) | EAT DB (°F) | EAT WB (°F) | LAT DB CLG | LAT WB CLG | TOTAL CAP (MBH) | EAT (°F) | LAT HTG | VOLTAGE | PHASE | HZ | AMPERAGE
tmpldvjvsq2.pdf | 3 | 0 | NOTES: 1. PROVIDE WITH MANUFACTURER'S STANDARD REMOTE CONTROLLER (PREMTB100). 2. PROVIDE WITH HIGH EFFICIENCY FILTER BOX (ZFBXM101A). 3.UNIT PROVIDED WITH FACTORY INSTALLED CONDENSATE PUMP. 4. PROVIDE WITH AUXILIARY HEATING KIT (PRAH1). | [10 empty] | FCU-1 | DUCTED | HALL 114 | 0.59 | 150 CFM | 24.2 | 80.5 | 62.4 | 55.0 °F | 54.0 °F | 27.3 | 63.9 | 83.8 °F | 208 V | 1 | 60 Hz | 2.00 A | CU-1 | 70 lb | LG | ARNU243M1A4 | 1,2,3
tmpldvjvsq2.pdf | 3 | 0 | NOTES: 1. PROVIDE WITH MANUFACTURER'S STANDARD REMOTE CONTROLLER (PREMTB100). 2. PROVIDE WITH HIGH EFFICIENCY FILTER BOX (ZFBXM101A). 3.UNIT PROVIDED WITH FACTORY INSTALLED CONDENSATE PUMP. 4. PROVIDE WITH AUXILIARY HEATING KIT (PRAH1). | [10 empty] | FCU-2 | DUCTED | BREAK ROOM 110 | 0.59 | 225 CFM | 24.2 | 86.7 | 66.1 | 54.2 °F | 51.7 °F | 27.3 | 57.1 | 76.9 °F | 208 V | 1 | 60 Hz | 2.00 A | CU-1 | 70 lb | LG | ARNU243M1A4 | 1,2,3
tmpldvjvsq2.pdf | 3 | 0 | NOTES: 1. PROVIDE WITH MANUFACTURER'S STANDARD REMOTE CONTROLLER (PREMTB100). 2. PROVIDE WITH HIGH EFFICIENCY FILTER BOX (ZFBXM101A). 3.UNIT PROVIDED WITH FACTORY INSTALLED CONDENSATE PUMP. 4. PROVIDE WITH AUXILIARY HEATING KIT (PRAH1). | [10 empty] | FCU-3 | DUCTED | BREAK ROOM 110 | 0.59 | 225 CFM | 24.2 | 86.7 | 66.1 | 54.2 °F | 51.7 °F | 27.3 | 57.1 | 76.9 °F | 208 V | 1 | 60 Hz | 2.00 A | CU-1 | 70 lb | LG | ARNU243M1A4 | 1,2,3
tmpldvjvsq2.pdf | 3 | 0 | NOTES: 1. PROVIDE WITH MANUFACTURER'S STANDARD REMOTE CONTROLLER (PREMTB100). 2. PROVIDE WITH HIGH EFFICIENCY FILTER BOX (ZFBXM101A). 3.UNIT PROVIDED WITH FACTORY INSTALLED CONDENSATE PUMP. 4. PROVIDE WITH AUXILIARY HEATING KIT (PRAH1). | [10 empty] | FCU-4 | DUCTED | HALL 105 | 0.59 | 30 CFM | 12.3 | 80.5 | 62.4 | 55.0 °F | 54.0 °F | 13.6 | 60.1 | 83.8 °F | 208 V | 1 | 60 Hz | 1.60 A | CU-1 | 56 lb | LG | ARNU123M1A4 | 1,2,3
tmpldvjvsq2.pdf | 3 | 0 | NOTES: 1. PROVIDE WITH MANUFACTURER'S STANDARD REMOTE CONTROLLER (PREMTB100). 2. PROVIDE WITH HIGH EFFICIENCY FILTER BOX (ZFBXM101A). 3.UNIT PROVIDED WITH FACTORY INSTALLED CONDENSATE PUMP. 4. PROVIDE WITH AUXILIARY HEATING KIT (PRAH1). | [10 empty] | FCU-5 | DUCTED | HALL 105 | 0.59 | 400 CFM | 12.3 | 104.0 | 65.0 | 55.0 °F | 54.0 °F | 13.6 | 55.0 | 83.8 °F | 208 V | 1 | 60 Hz | 1.60 A | CU-1 | 56 lb | LG | ARNU123M1A4 | 1,2,3
tmpldvjvsq2.pdf | 3 | 0 | NOTES: 1. PROVIDE WITH MANUFACTURER'S STANDARD REMOTE CONTROLLER (PREMTB100). 2. PROVIDE WITH HIGH EFFICIENCY FILTER BOX (ZFBXM101A). 3.UNIT PROVIDED WITH FACTORY INSTALLED CONDENSATE PUMP. 4. PROVIDE WITH AUXILIARY HEATING KIT (PRAH1). | [10 empty] | FCU-6 | DUCTED | SMALL ENGINE REPAIR 101 | 0.47 | 150 CFM | 12.3 | 91.4 | 66.2 | 55.0 °F | 50.4 °F | 13.6 | 51.9 | 85.3 °F | 208 V | 1 | 60 Hz | 1.60 A | CU-1 | 56 lb | LG | ARNU123M1A4 | 1,2,3
tmpldvjvsq2.pdf | 3 | 0 | NOTES: 1. PROVIDE WITH MANUFACTURER'S STANDARD REMOTE CONTROLLER (PREMTB100). 2. PROVIDE WITH HIGH EFFICIENCY FILTER BOX (ZFBXM101A). 3.UNIT PROVIDED WITH FACTORY INSTALLED CONDENSATE PUMP. 4. PROVIDE WITH AUXILIARY HEATING KIT (PRAH1). | [10 empty] | FCU-7 | DUCTED | SMALL ENGINE REPAIR 101 | 0.47 | 150 CFM | 12.3 | 91.4 | 66.2 | 55.0 °F | 50.4 °F | 13.6 | 51.9 | 85.3 °F | 208 V | 1 | 60 Hz | 1.60 A | CU-1 | 56 lb | LG | ARNU123M1A4 | 1,2,3,4
tmpldvjvsq2.pdf | 3 | 0 | NOTES: 1. PROVIDE WITH MANUFACTURER'S STANDARD REMOTE CONTROLLER (PREMTB100). 2. PROVIDE WITH HIGH EFFICIENCY FILTER BOX (ZFBXM101A). 3.UNIT PROVIDED WITH FACTORY INSTALLED CONDENSATE PUMP. 4. PROVIDE WITH AUXILIARY HEATING KIT (PRAH1). | [10 empty] | FCU-8 | CASSETTE | BUNK 1 108.1 | 0.00 | 30 CFM | 6.1 | 63.6 | 59.4 | 55.0 °F | 51.0 °F | 5.5 | 60.0 | 79.0 °F | 208 V | 1 | 60 Hz | 0.25 A | CU-1 | 7 lb | LG | ARNU053TFD4 | 1,2,3
tmpldvjvsq2.pdf | 3 | 0 | NOTES: 1. PROVIDE WITH MANUFACTURER'S STANDARD REMOTE CONTROLLER (PREMTB100). 2. PROVIDE WITH HIGH EFFICIENCY FILTER BOX (ZFBXM101A). 3.UNIT PROVIDED WITH FACTORY INSTALLED CONDENSATE PUMP. 4. PROVIDE WITH AUXILIARY HEATING KIT (PRAH1). | [10 empty] | FCU-9 | CASSETTE | BUNK 2 108.2 | 0.00 | 30 CFM | 6.1 | 63.6 | 59.4 | 55.0 °F | 51.0 °F | 5.5 | 60.0 | 79.0 °F | 208 V | 1 | 60 Hz | 0.25 A | CU-1 | 7 lb | LG | ARNU053TFD4 | 1,2,3
tmpldvjvsq2.pdf | 3 | 0 | NOTES: 1. PROVIDE WITH MANUFACTURER'S STANDARD REMOTE CONTROLLER (PREMTB100). 2. PROVIDE WITH HIGH EFFICIENCY FILTER BOX (ZFBXM101A). 3.UNIT PROVIDED WITH FACTORY INSTALLED CONDENSATE PUMP. 4. PROVIDE WITH AUXILIARY HEATING KIT (PRAH1). | [10 empty] | FCU-10 | CASSETTE | BUNK 3 108.3 | 0.00 | 30 CFM | 6.1 | 63.6 | 59.4 | 55.0 °F | 51.0 °F | 5.5 | 60.0 | 79.0 °F | 208 V | 1 | 60 Hz | 0.25 A | CU-1 | 7 lb | LG | ARNU053TFD4 | 1,2,3
tmpldvjvsq2.pdf | 3 | 0 | NOTES: 1. PROVIDE WITH MANUFACTURER'S STANDARD REMOTE CONTROLLER (PREMTB100). 2. PROVIDE WITH HIGH EFFICIENCY FILTER BOX (ZFBXM101A). 3.UNIT PROVIDED WITH FACTORY INSTALLED CONDENSATE PUMP. 4. PROVIDE WITH AUXILIARY HEATING KIT (PRAH1). | [10 empty] | FCU-11 | CASSETTE | BUNK 4 108.4 | 0.00 | 30 CFM | 6.1 | 63.6 | 59.4 | 55.0 °F | 51.0 °F | 5.5 | 60.0 | 79.0 °F | 208 V | 1 | 60 Hz | 0.25 A | CU-1 | 7 lb | LG | ARNU053TFD4 | 1,2,3
tmpldvjvsq2.pdf | 3 | 0 | NOTES: 1. PROVIDE WITH MANUFACTURER'S STANDARD REMOTE CONTROLLER (PREMTB100). 2. PROVIDE WITH HIGH EFFICIENCY FILTER BOX (ZFBXM101A). 3.UNIT PROVIDED WITH FACTORY INSTALLED CONDENSATE PUMP. 4. PROVIDE WITH AUXILIARY HEATING KIT (PRAH1). | [10 empty] | FCU-12 | CASSETTE | BUNK 5 108.5 | 0.00 | 30 CFM | 6.1 | 63.6 | 59.4 | 55.0 °F | 51.0 °F | 5.5 | 60.0 | 79.0 °F | 208 V | 1 | 60 Hz | 0.25 A | CU-1 | 7 lb | LG | ARNU053TFD4 | 1,2,3
tmpldvjvsq2.pdf | 3 | 0 | NOTES: 1. PROVIDE WITH MANUFACTURER'S STANDARD REMOTE CONTROLLER (PREMTB100). 2. PROVIDE WITH HIGH EFFICIENCY FILTER BOX (ZFBXM101A). 3.UNIT PROVIDED WITH FACTORY INSTALLED CONDENSATE PUMP. 4. PROVIDE WITH AUXILIARY HEATING KIT (PRAH1). | [10 empty] | FCU-13 | CASSETTE | BUNK 6 108.6 | 0.00 | 30 CFM | 6.1 | 63.6 | 59.4 | 55.0 °F | 51.0 °F | 5.5 | 60.0 | 79.0 °F | 208 V | 1 | 60 Hz | 0.25 A | CU-1 | 7 lb | LG | ARNU053TFD4 | 1,2,3
tmpldvjvsq2.pdf | 3 | 0 | NOTES: 1. PROVIDE WITH MANUFACTURER'S STANDARD REMOTE CONTROLLER (PREMTB100). 2. PROVIDE WITH HIGH EFFICIENCY FILTER BOX (ZFBXM101A). 3.UNIT PROVIDED WITH FACTORY INSTALLED CONDENSATE PUMP. 4. PROVIDE WITH AUXILIARY HEATING KIT (PRAH1). | [10 empty] | FCU-14 | DUCTED | STREETS STORAGE 201 | 0.59 | 150 CFM | 28.0 | 66.7 | 59.5 | 55.0 °F | 51.3 °F | 31.5 | 47.9 | 74.2 °F | 208 V | 1 | 60 Hz | 1.60 A | CU-1 | 56 lb | LG | ARNU123M1A4 | 1,2,3
tmpldvjvsq2.pdf | 3 | 0 | NOTES: 1. PROVIDE WITH MANUFACTURER'S STANDARD REMOTE CONTROLLER (PREMTB100). 2. PROVIDE WITH HIGH EFFICIENCY FILTER BOX (ZFBXM101A). 3.UNIT PROVIDED WITH FACTORY INSTALLED CONDENSATE PUMP. 4. PROVIDE WITH AUXILIARY HEATING KIT (PRAH1). | [10 empty] | FCU-15 | DUCTED | STREETS STORAGE 201 | 0.59 | 150 CFM | 28.0 | 66.7 | 59.5 | 55.0 °F | 51.3 °F | 31.5 | 47.9 | 74.2 °F | 208 V | 1 | 60 Hz | 1.60 A | CU-1 | 56 lb | LG | ARNU123M1A4 | 1,2,3
tmpldvjvsq2.pdf | 3 | 0 | NOTES: 1. PROVIDE WITH MANUFACTURER'S STANDARD REMOTE CONTROLLER (PREMTB100). 2. PROVIDE WITH HIGH EFFICIENCY FILTER BOX (ZFBXM101A). 3.UNIT PROVIDED WITH FACTORY INSTALLED CONDENSATE PUMP. 4. PROVIDE WITH AUXILIARY HEATING KIT (PRAH1). | [10 empty] | FCU-16 | DUCTED | STREETS STORAGE 201 | 0.59 | 150 CFM | 28.0 | 66.7 | 59.5 | 55.0 °F | 51.3 °F | 31.5 | 47.9 | 74.2 °F | 208 V | 1 | 60 Hz | 2.00 A | CU-1 | 70 lb | LG | ARNU243M1A4 | 1,2,3
tmpldvjvsq2.pdf | 3 | 1 | [8 empty] | Kimley-Horn's client and for a particular purpose. Any other
tmpldvjvsq2.pdf | 3 | 1 | [8 empty] | use or reliance is without liability to Kimley-Horn.
tmpldvjvsq2.pdf | 3 | 2 | NOTES: 1. MANUFACTURER PROVIDES THIS UNIT AS A COMBINATION OF MODELS ARUM096BTE5 AND ARUM168BTE5 2. PROVIDE WITH THREE HEAT RECOVERY UNITS MODEL # PRHR063A (ELECTRICAL INFORMATION: 208V, 1 PHASE, 60 HZ, 0.27 MCA). |  |  |  | SUMMER AMBIENT |  |  | EER | [9 empty] | WINTER AMBIENT DB (°F) |  | PHASE | HZ |  | MOCP |  | VOLTAGE | [8 empty] | TOTAL CAP (MBH) | REFRIGERANT TYPE | TOTAL CAP (MBH) | MCA
tmpldvjvsq2.pdf | 3 | 2 | NOTES: 1. MANUFACTURER PROVIDES THIS UNIT AS A COMBINATION OF MODELS ARUM096BTE5 AND ARUM168BTE5 2. PROVIDE WITH THREE HEAT RECOVERY UNITS MODEL # PRHR063A (ELECTRICAL INFORMATION: 208V, 1 PHASE, 60 HZ, 0.27 MCA). |  |  |  | DB (°F) |  | WB (°F)
tmpldvjvsq2.pdf | 3 | 2 | NOTES: 1. MANUFACTURER PROVIDES THIS UNIT AS A COMBINATION OF MODELS ARUM096BTE5 AND ARUM168BTE5 2. PROVIDE WITH THREE HEAT RECOVERY UNITS MODEL # PRHR063A (ELECTRICAL INFORMATION: 208V, 1 PHASE, 60 HZ, 0.27 MCA). |  |  |  | 94.7 |  | 60.3 | 9.7 |  |  |  | CU-1 | [5 empty] | 18.2 |  | 3 | 60 Hz |  | 40 A |  | 208 V |  |  |  |  | 510 lb | LG | ARUM264BTE5 | 1,2 | 96.0 | R410a | 108.0 | 29 A
tmpldvjvsq2.pdf | 3 | 3 | NOTES: 1. PROVIDE SINGLE POINT POWER CONNECTION. 2. PROVIDE 120V, 20 AMP DUPLEX CONVENIENCE RECEPTABLE MOUNTED TO UNIT. COORDINATE WITH ELECTRICAL CONTRACTOR. 3. SELECT EQUIPMENT FOR ELEVATION OF 5,300 FEET ABOVE SEA LEVEL. 4. TOTAL HEATING CAPACITY INCLUDES THE HEAT PUMP HEATING COIL CAPACITY AT THE AMBIENT DRY BULB TEMPERATURE LISTED. 5. PROVIDE WITH MANUFACTURER'S 7 DAY PROGRAMMABLE THERMOSTAT. 6. PROVIDE WITH 2" PLEATED MERV 8 FILTERS. 7. PROVIDE WITH SUPPLY AIR SMOKE DAMPER. 8. PROVIDE ECONOMIZER WITH BAROMETRIC RELIEF. | [6 empty] | ESP (IN W.C.) | [6 empty] | AIRFLOW (CFM) |  | TOTAL CAP (MBH) |  | LAT |  | AMBIENT CONDITIONS |  | EER |  | VOLTAGE | LAT (°F) | AMBIENT DB (°F) | [11 empty] | EAT | TOTAL CAP. (MBH) | EAT (°F) | PHASE | HZ | MCA | MOCP
tmpldvjvsq2.pdf | 3 | 3 | NOTES: 1. PROVIDE SINGLE POINT POWER CONNECTION. 2. PROVIDE 120V, 20 AMP DUPLEX CONVENIENCE RECEPTABLE MOUNTED TO UNIT. COORDINATE WITH ELECTRICAL CONTRACTOR. 3. SELECT EQUIPMENT FOR ELEVATION OF 5,300 FEET ABOVE SEA LEVEL. 4. TOTAL HEATING CAPACITY INCLUDES THE HEAT PUMP HEATING COIL CAPACITY AT THE AMBIENT DRY BULB TEMPERATURE LISTED. 5. PROVIDE WITH MANUFACTURER'S 7 DAY PROGRAMMABLE THERMOSTAT. 6. PROVIDE WITH 2" PLEATED MERV 8 FILTERS. 7. PROVIDE WITH SUPPLY AIR SMOKE DAMPER. 8. PROVIDE ECONOMIZER WITH BAROMETRIC RELIEF. | [16 empty] | WB (°F) | DB (°F) | WB (°F) | DB (°F) | [15 empty] | WB (°F) |  | DB (°F)
tmpldvjvsq2.pdf | 3 | 3 | NOTES: 1. PROVIDE SINGLE POINT POWER CONNECTION. 2. PROVIDE 120V, 20 AMP DUPLEX CONVENIENCE RECEPTABLE MOUNTED TO UNIT. COORDINATE WITH ELECTRICAL CONTRACTOR. 3. SELECT EQUIPMENT FOR ELEVATION OF 5,300 FEET ABOVE SEA LEVEL. 4. TOTAL HEATING CAPACITY INCLUDES THE HEAT PUMP HEATING COIL CAPACITY AT THE AMBIENT DRY BULB TEMPERATURE LISTED. 5. PROVIDE WITH MANUFACTURER'S 7 DAY PROGRAMMABLE THERMOSTAT. 6. PROVIDE WITH 2" PLEATED MERV 8 FILTERS. 7. PROVIDE WITH SUPPLY AIR SMOKE DAMPER. 8. PROVIDE ECONOMIZER WITH BAROMETRIC RELIEF. | [6 empty] | 1.03 |  |  |  | AHU-1 | PACKAGED |  | 3000 |  | 73.0 | 60.0 | 53.5 | 51.0 | 95.0 |  | 11.2 |  | 208 V | 72.4 | 4.0 |  |  |  | TRANE | TSJ090A3S0G | 1-8 |  |  |  | 60.0 | 0 | 78.0 | 61.5 | 50.0 | 3 | 60 Hz | 60 A | 60 A | 925
tmpldvjvsq2.pdf | 3 | 3 | NOTES: 1. PROVIDE SINGLE POINT POWER CONNECTION. 2. PROVIDE 120V, 20 AMP DUPLEX CONVENIENCE RECEPTABLE MOUNTED TO UNIT. COORDINATE WITH ELECTRICAL CONTRACTOR. 3. SELECT EQUIPMENT FOR ELEVATION OF 5,300 FEET ABOVE SEA LEVEL. 4. TOTAL HEATING CAPACITY INCLUDES THE HEAT PUMP HEATING COIL CAPACITY AT THE AMBIENT DRY BULB TEMPERATURE LISTED. 5. PROVIDE WITH MANUFACTURER'S 7 DAY PROGRAMMABLE THERMOSTAT. 6. PROVIDE WITH 2" PLEATED MERV 8 FILTERS. 7. PROVIDE WITH SUPPLY AIR SMOKE DAMPER. 8. PROVIDE ECONOMIZER WITH BAROMETRIC RELIEF. | [6 empty] | 1.03 |  |  |  | AHU-2 | PACKAGED |  | 3000 |  | 73.0 | 60.0 | 53.5 | 51.0 | 95.0 |  | 11.2 |  | 208 V | 72.4 | 4.0 |  |  |  | TRANE | TSJ090A3S0G | 1-8 |  |  |  | 60.0 | 0 | 78.0 | 61.5 | 50.0 | 3 | 60 Hz | 60 A | 60 A | 925
tmpldvjvsq2.pdf | 3 | 4 | [9 empty] | DIVISION
tmpldvjvsq2.pdf | 3 | 5 | NOTES: 1. PROVIDE 3/4" MESH ALUMINUM BIRD SCREEN. 2. PROVIDE STANDARD MILL FINISH. 3. FRAME SHALL MATCH WALL CONSTRUCTION. COORDINATE WITH ARCHITECT. 4. PROVIDE WITH MANUFACTURER'S BACKDRAFT DAMPER. 5. PROVIDE WITH GREENHECK MODEL BR-42 BACKDRAFT DAMPER. | [5 empty] | HEIGHT | [40 empty] | WIDTH
tmpldvjvsq2.pdf | 3 | 5 | NOTES: 1. PROVIDE 3/4" MESH ALUMINUM BIRD SCREEN. 2. PROVIDE STANDARD MILL FINISH. 3. FRAME SHALL MATCH WALL CONSTRUCTION. COORDINATE WITH ARCHITECT. 4. PROVIDE WITH MANUFACTURER'S BACKDRAFT DAMPER. 5. PROVIDE WITH GREENHECK MODEL BR-42 BACKDRAFT DAMPER. | [5 empty] | 3' - 10" |  |  |  |  | L-1 | [18 empty] | GREENHECK | ESD-435 | 1-3,5 | [13 empty] | EMERGENCY INTAKE | 3' - 6" | 3700 | 7.4 ft² | 500 FPM | 0.07
tmpldvjvsq2.pdf | 3 | 5 | NOTES: 1. PROVIDE 3/4" MESH ALUMINUM BIRD SCREEN. 2. PROVIDE STANDARD MILL FINISH. 3. FRAME SHALL MATCH WALL CONSTRUCTION. COORDINATE WITH ARCHITECT. 4. PROVIDE WITH MANUFACTURER'S BACKDRAFT DAMPER. 5. PROVIDE WITH GREENHECK MODEL BR-42 BACKDRAFT DAMPER. | [5 empty] | 1' - 2" |  |  |  |  | L-2 | [18 empty] | GREENHECK | ESD-435 | 1-4 | [13 empty] | GENERAL INTAKE | 1' - 6" | 300 | 0.6 ft² | 500 FPM | 0.07
tmpldvjvsq2.pdf | 3 | 5 | NOTES: 1. PROVIDE 3/4" MESH ALUMINUM BIRD SCREEN. 2. PROVIDE STANDARD MILL FINISH. 3. FRAME SHALL MATCH WALL CONSTRUCTION. COORDINATE WITH ARCHITECT. 4. PROVIDE WITH MANUFACTURER'S BACKDRAFT DAMPER. 5. PROVIDE WITH GREENHECK MODEL BR-42 BACKDRAFT DAMPER. | [5 empty] | 0' - 8" |  |  |  |  | L-3 | [18 empty] | GREENHECK | ESD-435 | 1-4 | [13 empty] | INTAKE OR EXHAUST | 0' - 8" | 120 | 0.5 ft² | 500 FPM | 0.20
tmpldvjvsq2.pdf | 3 | 7 | NOTES: 1. NECK SIZE SHOWN ON DRAWINGS. PROVIDE BRANCH DUCT TO MATCH NECK SIZE UNLESS OTHERWISE SHOWN ON DRAWINGS. 2. DOUBLE DEFLECTION BARS SHALL BE ADJUSTABLE. 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. 4. PROVIDE OPPOSED BLADE DAMPER ADJUSTABLE FRM FACE OF DEVICE. | [10 empty] | CD-1 | [18 empty] | TITUS | TMS | 1,4 | [18 empty] | 0.10 | STEEL | LOUVERED | 24"X24" | LAY-IN | WHITE | 1000 CFM | 30
tmpldvjvsq2.pdf | 3 | 7 | NOTES: 1. NECK SIZE SHOWN ON DRAWINGS. PROVIDE BRANCH DUCT TO MATCH NECK SIZE UNLESS OTHERWISE SHOWN ON DRAWINGS. 2. DOUBLE DEFLECTION BARS SHALL BE ADJUSTABLE. 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. 4. PROVIDE OPPOSED BLADE DAMPER ADJUSTABLE FRM FACE OF DEVICE. | [10 empty] | CD-2 | [18 empty] | TITUS | TMS | 1,4 | [18 empty] | 0.10 | STEEL | LOUVERED | 12"X12" | LAY-IN | WHITE | 244 CFM | 30
tmpldvjvsq2.pdf | 3 | 7 | NOTES: 1. NECK SIZE SHOWN ON DRAWINGS. PROVIDE BRANCH DUCT TO MATCH NECK SIZE UNLESS OTHERWISE SHOWN ON DRAWINGS. 2. DOUBLE DEFLECTION BARS SHALL BE ADJUSTABLE. 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. 4. PROVIDE OPPOSED BLADE DAMPER ADJUSTABLE FRM FACE OF DEVICE. | [10 empty] | EG-1 | [18 empty] | TITUS | PAR | 1,4 | [18 empty] | 0.10 | STEEL | LOUVERED | 12"X12" | LAY-IN | WHITE | 244 CFM | 30
tmpldvjvsq2.pdf | 3 | 7 | NOTES: 1. NECK SIZE SHOWN ON DRAWINGS. PROVIDE BRANCH DUCT TO MATCH NECK SIZE UNLESS OTHERWISE SHOWN ON DRAWINGS. 2. DOUBLE DEFLECTION BARS SHALL BE ADJUSTABLE. 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. 4. PROVIDE OPPOSED BLADE DAMPER ADJUSTABLE FRM FACE OF DEVICE. | [10 empty] | RG-1 | [18 empty] | TITUS | PAR | 1,4 | [18 empty] | 0.08 | STEEL | PERFORATED | 24"X24" | LAY-IN | WHITE | 1000 CFM | 30
tmpldvjvsq2.pdf | 3 | 7 | NOTES: 1. NECK SIZE SHOWN ON DRAWINGS. PROVIDE BRANCH DUCT TO MATCH NECK SIZE UNLESS OTHERWISE SHOWN ON DRAWINGS. 2. DOUBLE DEFLECTION BARS SHALL BE ADJUSTABLE. 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. 4. PROVIDE OPPOSED BLADE DAMPER ADJUSTABLE FRM FACE OF DEVICE. | [10 empty] | RG-2 | [18 empty] | TITUS | 350R | 2,3 | [18 empty] | 0.10 | STEEL | LOUVERED | 28"X28" | SURFACE | WHITE | 3000 CFM | 30
tmpldvjvsq2.pdf | 3 | 7 | NOTES: 1. NECK SIZE SHOWN ON DRAWINGS. PROVIDE BRANCH DUCT TO MATCH NECK SIZE UNLESS OTHERWISE SHOWN ON DRAWINGS. 2. DOUBLE DEFLECTION BARS SHALL BE ADJUSTABLE. 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. 4. PROVIDE OPPOSED BLADE DAMPER ADJUSTABLE FRM FACE OF DEVICE. | [10 empty] | SG-1 | [18 empty] | TITUS | DL-SV | 2,3 | [18 empty] | 0.10 | ALUMINUM | DRUM | 20"X10" | SURFACE | WHITE | 1000 CFM | 30
tmpldvjvsq2.pdf | 3 | 7 | NOTES: 1. NECK SIZE SHOWN ON DRAWINGS. PROVIDE BRANCH DUCT TO MATCH NECK SIZE UNLESS OTHERWISE SHOWN ON DRAWINGS. 2. DOUBLE DEFLECTION BARS SHALL BE ADJUSTABLE. 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. 4. PROVIDE OPPOSED BLADE DAMPER ADJUSTABLE FRM FACE OF DEVICE. | [10 empty] | SG-2 | [18 empty] | TITUS | DL-SV | 2,3 | [18 empty] | 0.10 | ALUMINUM | DRUM | 10"X6" | SURFACE | WHITE | 200 CFM | 30
tmpldvjvsq2.pdf | 4 | 0 | NOTES: 1. MOUNT 10 FEET ABOVE FINISHED FLOOR WITHOUT OBSTRUCTING AIRFLOW. 2. PROVIDE WITH UNIT MOUNTED THERMOSTAT. 3. PROVIDE NECESSARY MOUNTING BRACKET AND ACCESSORIES FOR WALL MOUNTING. | [16 empty] | PHASE | HZ | [5 empty] | MCA | [9 empty] | MOCP | CAPACITY (KW) |  |  | VOLTAGE
tmpldvjvsq2.pdf | 4 | 0 | NOTES: 1. MOUNT 10 FEET ABOVE FINISHED FLOOR WITHOUT OBSTRUCTING AIRFLOW. 2. PROVIDE WITH UNIT MOUNTED THERMOSTAT. 3. PROVIDE NECESSARY MOUNTING BRACKET AND ACCESSORIES FOR WALL MOUNTING. | [10 empty] | UH-1 |  | FIRE RISER ROOM |  |  |  | 1 | 60 | [5 empty] | 0 A |  |  |  |  | 20 lb | REZNOR | EGW | 1-3 |  | 0 A | 6824.0 |  |  | 208 V | [9 empty] | 300
tmpldvjvsq2.pdf | 4 | 1 | [8 empty] | Kimley-Horn's client and for a particular purpose. Any other
tmpldvjvsq2.pdf | 4 | 1 | [8 empty] | use or reliance is without liability to Kimley-Horn.
tmpldvjvsq2.pdf | 4 | 2 | NOTES: 1. PROVIDE WITH 6" TO 4" ROUND REDUCES. 2. PROVIDE WALL CAL WITH INTEGRAL BACKDRAFT DAMPER. 3. FAN TO OPERATE OFF ROOMS LIGHT SWITCH, SEE ELECTRICAL DRAWINGS. 4. FAN SHALL BE OPERATED INTEGRATED TO GAS DETECTION SYSTEM TO ACTIVATE BASED ON CO AND NO2 DETECTION. 5. PROVIDE WITH BIDSCREEN OVER OPENING AND GRAVITY BACKDRAFT DAMPER. 6. FAN TO OPERATE CONTINUOUSLY, SEE ELECTRICAL FOR WALL SWITCH LOCATION. | [16 empty] | MOTOR | [6 empty] | VOLTAGE | [9 empty] | PHASE |  |  |  | HZ
tmpldvjvsq2.pdf | 4 | 2 | NOTES: 1. PROVIDE WITH 6" TO 4" ROUND REDUCES. 2. PROVIDE WALL CAL WITH INTEGRAL BACKDRAFT DAMPER. 3. FAN TO OPERATE OFF ROOMS LIGHT SWITCH, SEE ELECTRICAL DRAWINGS. 4. FAN SHALL BE OPERATED INTEGRATED TO GAS DETECTION SYSTEM TO ACTIVATE BASED ON CO AND NO2 DETECTION. 5. PROVIDE WITH BIDSCREEN OVER OPENING AND GRAVITY BACKDRAFT DAMPER. 6. FAN TO OPERATE CONTINUOUSLY, SEE ELECTRICAL FOR WALL SWITCH LOCATION. | [16 empty] | HP
tmpldvjvsq2.pdf | 4 | 2 | NOTES: 1. PROVIDE WITH 6" TO 4" ROUND REDUCES. 2. PROVIDE WALL CAL WITH INTEGRAL BACKDRAFT DAMPER. 3. FAN TO OPERATE OFF ROOMS LIGHT SWITCH, SEE ELECTRICAL DRAWINGS. 4. FAN SHALL BE OPERATED INTEGRATED TO GAS DETECTION SYSTEM TO ACTIVATE BASED ON CO AND NO2 DETECTION. 5. PROVIDE WITH BIDSCREEN OVER OPENING AND GRAVITY BACKDRAFT DAMPER. 6. FAN TO OPERATE CONTINUOUSLY, SEE ELECTRICAL FOR WALL SWITCH LOCATION. | [10 empty] | EF-1 | [5 empty] | 0.01 | [6 empty] | 115 V |  |  |  |  | 12 lb | GREENHECK | SP-A90 | 1,2,3 |  | 1 |  |  |  | 60 | [9 empty] | 60 | [10 empty] | CELING | 0.10
tmpldvjvsq2.pdf | 4 | 2 | NOTES: 1. PROVIDE WITH 6" TO 4" ROUND REDUCES. 2. PROVIDE WALL CAL WITH INTEGRAL BACKDRAFT DAMPER. 3. FAN TO OPERATE OFF ROOMS LIGHT SWITCH, SEE ELECTRICAL DRAWINGS. 4. FAN SHALL BE OPERATED INTEGRATED TO GAS DETECTION SYSTEM TO ACTIVATE BASED ON CO AND NO2 DETECTION. 5. PROVIDE WITH BIDSCREEN OVER OPENING AND GRAVITY BACKDRAFT DAMPER. 6. FAN TO OPERATE CONTINUOUSLY, SEE ELECTRICAL FOR WALL SWITCH LOCATION. | [10 empty] | EF-2 | [5 empty] | 0.01 | [6 empty] | 115 V |  |  |  |  | 12 lb | GREENHECK | SP-A90 | 1,2,3 |  | 1 |  |  |  | 60 | [9 empty] | 60 | [10 empty] | CEILING | 0.10
tmpldvjvsq2.pdf | 4 | 2 | NOTES: 1. PROVIDE WITH 6" TO 4" ROUND REDUCES. 2. PROVIDE WALL CAL WITH INTEGRAL BACKDRAFT DAMPER. 3. FAN TO OPERATE OFF ROOMS LIGHT SWITCH, SEE ELECTRICAL DRAWINGS. 4. FAN SHALL BE OPERATED INTEGRATED TO GAS DETECTION SYSTEM TO ACTIVATE BASED ON CO AND NO2 DETECTION. 5. PROVIDE WITH BIDSCREEN OVER OPENING AND GRAVITY BACKDRAFT DAMPER. 6. FAN TO OPERATE CONTINUOUSLY, SEE ELECTRICAL FOR WALL SWITCH LOCATION. | [10 empty] | EF-3 | [5 empty] | 0.01 | [6 empty] | 115 V |  |  |  |  | 12 lb | GREENHECK | SP-A90 | 1,2,3 |  | 1 |  |  |  | 60 | [9 empty] | 60 | [10 empty] | CEILING | 0.10
tmpldvjvsq2.pdf | 4 | 2 | NOTES: 1. PROVIDE WITH 6" TO 4" ROUND REDUCES. 2. PROVIDE WALL CAL WITH INTEGRAL BACKDRAFT DAMPER. 3. FAN TO OPERATE OFF ROOMS LIGHT SWITCH, SEE ELECTRICAL DRAWINGS. 4. FAN SHALL BE OPERATED INTEGRATED TO GAS DETECTION SYSTEM TO ACTIVATE BASED ON CO AND NO2 DETECTION. 5. PROVIDE WITH BIDSCREEN OVER OPENING AND GRAVITY BACKDRAFT DAMPER. 6. FAN TO OPERATE CONTINUOUSLY, SEE ELECTRICAL FOR WALL SWITCH LOCATION. | [10 empty] | EF-4 | [5 empty] | 0.01 | [6 empty] | 115 V |  |  |  |  | 51 lb | GREENHECK | SQ-95-VG | 1,2,3 |  | 1 |  |  |  | 60 | [9 empty] | 250 | [10 empty] | INLINE | 0.10
tmpldvjvsq2.pdf | 4 | 2 | NOTES: 1. PROVIDE WITH 6" TO 4" ROUND REDUCES. 2. PROVIDE WALL CAL WITH INTEGRAL BACKDRAFT DAMPER. 3. FAN TO OPERATE OFF ROOMS LIGHT SWITCH, SEE ELECTRICAL DRAWINGS. 4. FAN SHALL BE OPERATED INTEGRATED TO GAS DETECTION SYSTEM TO ACTIVATE BASED ON CO AND NO2 DETECTION. 5. PROVIDE WITH BIDSCREEN OVER OPENING AND GRAVITY BACKDRAFT DAMPER. 6. FAN TO OPERATE CONTINUOUSLY, SEE ELECTRICAL FOR WALL SWITCH LOCATION. | [10 empty] | EF-5 | [5 empty] | 0.01 | [6 empty] | 115 V |  |  |  |  | 51 lb | GREENHECK | SQ-95-VG | 1,2,3 |  | 1 |  |  |  | 60 | [9 empty] | 150 | [10 empty] | INLINE | 0.10
tmpldvjvsq2.pdf | 4 | 2 | NOTES: 1. PROVIDE WITH 6" TO 4" ROUND REDUCES. 2. PROVIDE WALL CAL WITH INTEGRAL BACKDRAFT DAMPER. 3. FAN TO OPERATE OFF ROOMS LIGHT SWITCH, SEE ELECTRICAL DRAWINGS. 4. FAN SHALL BE OPERATED INTEGRATED TO GAS DETECTION SYSTEM TO ACTIVATE BASED ON CO AND NO2 DETECTION. 5. PROVIDE WITH BIDSCREEN OVER OPENING AND GRAVITY BACKDRAFT DAMPER. 6. FAN TO OPERATE CONTINUOUSLY, SEE ELECTRICAL FOR WALL SWITCH LOCATION. | [10 empty] | EF-6 | [5 empty] | 0.01 | [6 empty] | 115 V |  |  |  |  | 24 lb | GREENHECK | SP-A250-QD | 6 |  | 1 |  |  |  | 60 | [9 empty] | 270 | [10 empty] | CEILING | 0.13
tmpldvjvsq2.pdf | 4 | 2 | NOTES: 1. PROVIDE WITH 6" TO 4" ROUND REDUCES. 2. PROVIDE WALL CAL WITH INTEGRAL BACKDRAFT DAMPER. 3. FAN TO OPERATE OFF ROOMS LIGHT SWITCH, SEE ELECTRICAL DRAWINGS. 4. FAN SHALL BE OPERATED INTEGRATED TO GAS DETECTION SYSTEM TO ACTIVATE BASED ON CO AND NO2 DETECTION. 5. PROVIDE WITH BIDSCREEN OVER OPENING AND GRAVITY BACKDRAFT DAMPER. 6. FAN TO OPERATE CONTINUOUSLY, SEE ELECTRICAL FOR WALL SWITCH LOCATION. | [10 empty] | EF-7 | [5 empty] | 0.1 | [6 empty] | 115 V |  |  |  |  | 29 lb | GREENHECK | CUE-70-VG | 5,6 |  | 1 |  |  |  | 60 | [9 empty] | 300 | [10 empty] | WALL | 0.15
tmpldvjvsq2.pdf | 4 | 2 | NOTES: 1. PROVIDE WITH 6" TO 4" ROUND REDUCES. 2. PROVIDE WALL CAL WITH INTEGRAL BACKDRAFT DAMPER. 3. FAN TO OPERATE OFF ROOMS LIGHT SWITCH, SEE ELECTRICAL DRAWINGS. 4. FAN SHALL BE OPERATED INTEGRATED TO GAS DETECTION SYSTEM TO ACTIVATE BASED ON CO AND NO2 DETECTION. 5. PROVIDE WITH BIDSCREEN OVER OPENING AND GRAVITY BACKDRAFT DAMPER. 6. FAN TO OPERATE CONTINUOUSLY, SEE ELECTRICAL FOR WALL SWITCH LOCATION. | [10 empty] | EF-8 | [5 empty] | 0.33 | [6 empty] | 115 V |  |  |  |  | 174 lb | GREENHECK | CUBE-220-20 | 4,5 |  | 1 |  |  |  | 60 | [9 empty] | 3700 | [10 empty] | WALL | 0.13
tmpldvjvsq2.pdf | 4 | 2 | NOTES: 1. PROVIDE WITH 6" TO 4" ROUND REDUCES. 2. PROVIDE WALL CAL WITH INTEGRAL BACKDRAFT DAMPER. 3. FAN TO OPERATE OFF ROOMS LIGHT SWITCH, SEE ELECTRICAL DRAWINGS. 4. FAN SHALL BE OPERATED INTEGRATED TO GAS DETECTION SYSTEM TO ACTIVATE BASED ON CO AND NO2 DETECTION. 5. PROVIDE WITH BIDSCREEN OVER OPENING AND GRAVITY BACKDRAFT DAMPER. 6. FAN TO OPERATE CONTINUOUSLY, SEE ELECTRICAL FOR WALL SWITCH LOCATION. | [10 empty] | EF-9 | [5 empty] | 0.33 | [6 empty] | 115 V |  |  |  |  | 174 lb | GREENHECK | CUBE-220-20 | 4,5 |  | 1 |  |  |  | 60 | [9 empty] | 3700 | [10 empty] | WALL | 0.13
tmpldvjvsq2.pdf | 4 | 2 | NOTES: 1. PROVIDE WITH 6" TO 4" ROUND REDUCES. 2. PROVIDE WALL CAL WITH INTEGRAL BACKDRAFT DAMPER. 3. FAN TO OPERATE OFF ROOMS LIGHT SWITCH, SEE ELECTRICAL DRAWINGS. 4. FAN SHALL BE OPERATED INTEGRATED TO GAS DETECTION SYSTEM TO ACTIVATE BASED ON CO AND NO2 DETECTION. 5. PROVIDE WITH BIDSCREEN OVER OPENING AND GRAVITY BACKDRAFT DAMPER. 6. FAN TO OPERATE CONTINUOUSLY, SEE ELECTRICAL FOR WALL SWITCH LOCATION. | [10 empty] | EF-10 | [5 empty] | 0.1 | [6 empty] | 115 V |  |  |  |  | 29 lb | GREENHECK | CUE-70-VG | 5,6 |  | 1 |  |  |  | 60 | [9 empty] | 300 | [10 empty] | WALL | 0.15
tmpldvjvsq2.pdf | 4 | 3 | AIR COMPRESSOR SCHEDULE | [10 empty] | AIR-1 | [17 empty] | 1000 lb | QUINCY | QT-10 | [29 empty] | 120 | VERTICAL | 35 CFM | 968 | 208 V | 3 | 60 Hz
tmpldvjvsq2.pdf | 4 | 4 | [9 empty] | DIVISION

## PlanCounts
file_name | plan | mark | mark_type | count
tmpldvjvsq2.pdf | MECHANICAL FLOOR PLAN - GROUND FLOOR | CD-1 | CD | 1
tmpldvjvsq2.pdf | MECHANICAL FLOOR PLAN - GROUND FLOOR | L-1 | L | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | AHU-1 | AHU | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | AHU-2 | AHU | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | CD-1 | CD | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | CD-2 | CD | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | CU-1 | CU | 25
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | EG-1 | EG | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | FCU-1 | FCU | 8
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | FCU-10 | FCU | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | FCU-11 | FCU | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | FCU-12 | FCU | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | FCU-13 | FCU | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | FCU-14 | FCU | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | FCU-15 | FCU | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | FCU-16 | FCU | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | FCU-2 | FCU | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | FCU-3 | FCU | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | FCU-4 | FCU | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | FCU-5 | FCU | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | FCU-6 | FCU | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | FCU-7 | FCU | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | FCU-8 | FCU | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | FCU-9 | FCU | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | L-1 | L | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | L-2 | L | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | L-3 | L | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | RG-1 | RG | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | RG-2 | RG | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | SG-1 | SG | 1
tmpldvjvsq2.pdf | 3. FRAME TO MATCH CEILING/WALL CONSTRUCTION, COORDINATE WITH ARCHITECTURAL REFLECTED CEILING/WALL PLAN. | SG-2 | SG | 1
tmpldvjvsq2.pdf | FLOOR PLAN - | CD-1 | CD | 25
tmpldvjvsq2.pdf | FLOOR PLAN - | EG-1 | EG | 4
tmpldvjvsq2.pdf | FLOOR PLAN - | RG-1 | RG | 5
tmpldvjvsq2.pdf | FLOOR PLAN - | RG-2 | RG | 2
tmpldvjvsq2.pdf | FLOOR PLAN - | SG-1 | SG | 10
tmpldvjvsq2.pdf | FLOOR PLAN - | SG-2 | SG | 18